## En_Bal_Calc
Energy Balance Example
Energy Balance: Small Food Processing Plant
Description | Size | Units | Oper hr | Load | kWh | MMBtu | % total
Electrical Usage
VSD screw | 125 | HP | 8760 | 0.5 | 439177.4194 | 1498.4734 | 9.988%
Recip backup | 50 | HP | 500 | 0.7 | 14505.5556 | 49.493 | 0.3299% | Cumulative Energy Usage
Chiller | 100 | tons | 8760 | 0.5 | 350400 | 1195.5648 | 7.969% | chiller | 11.56%
Air handlers | 20 | HP | 8760 | 0.75 | 108916 | 371.6214 | 2.477% | process | 3.981%
Cooling tower | 15 | HP | 8760 | 0.45 | 49012.2 | 167.2296 | 1.115%
Refrigeration | 3 | tons | 8760 | 0.5 | 10512 | 35.8669 | 0.2391%
Process pumps | 50 | HP | 6600 | 0.6 | 164120 | 559.9774 | 3.732%
Votator | 20 | HP | 3300 | 0.4 | 21882.6667 | 74.6637 | 0.4977%
Homogenizer | 40 | HP | 3300 | 0.4 | 43765.3333 | 149.3273 | 0.9953%
Plant lights | 69 | kW | 6600 | 1 | 455400 | 1553.8248 | 10.36%
Process motors | 50 | HP | 6600 | 0.4 | 109413.3333 | 373.3183 | 2.488%
Misc electrical use |  |  |  |  | 352695.4918 | 1203.397 | 8.021%
Natural Gas Usage
Boiler | 25 | bHP | 6600 | 0.35 |  | 6909.375 | 46.05%
Water heater | 300000 | Btuh | 8760 | 0.2 |  | 525.6 | 3.503%
Misc gas use | [5 empty] | 335.025 | 2.233%
Plant total | [5 empty] | 15002.7576 | 100%
Enterprise Annual Energy Usage |  |  |  | Equipment use = Plant consumption
Source | Usage | Units
Natural gas | 7770 | MMBtu
Electricity | 2119800 | kWh
Combined Btu | 15002.7576 | MMBtu
Energy Balance Example
50001 Ready Navigator (https://navigator.industrialenergytools.com | [5 empty] | February 2017
© 2017 Georgia Tech Research Corporation and U.S. Department of Energy